Impacts of high penetration of heat pumps to distribution network

# introduction

During recent years, the use of energy has changed because new kinds of loads have been connected to the distribution network. Three main issues have driven this change of loads. One is the green house effect and second is the energy price, which has risen, and third is the reduced manufacturing costs of devices.

The main act in preventing the green house effect and global warming is to decrease carbon dioxide emissions. Because of this more and more loads, which are reducing carbon dioxide emissions, have entered in the market. For example compact fluorescent lamps are one group of such loads. Replacing incandescent bulbs with compact fluorescent lamps is one such act that should reduce carbon dioxide emissions because of the efficient light produce of compact fluorescent lamps compared with incandescent bulbs. The result of European Commission Regulation number 244/2009 is that incandescent bulbs will be gradually phased out from the market. [1, 6]

The increasing energy price has affected the use of energy so that customers have invested in devices which reduce costs and energy consumption. One good example of this kind of behavior is to replace an oil heating system with a heat pump or to add an air-to-air heat pump in complement electric heating. In Finland support from government has speeded up this change [4]. Figure 1 shows the number of installations of different types of heat pumps in Finland during the years 1996-2008. As shown in Figure 1 the number of heat pumps has grown very rapidly during past few years [2]. The growing trend has been the same all over Europe. The overall percentage of heat pumps of all heating types is not very massive in Europe but for example in Sweden heat pumps are the most common heating system in single-family houses with an approximately 34 % share of all. [3]

Figure 1	Number of installations of different heat pump types in Finland during years 1996-2008.[2]

Different heat pumps may have different effects on electrical energy consumption and to the way electricity is used. For example, if an oil heating system is replaced with a ground source heat pump, the overall consumption of electrical energy of a house will increase, but if an air-to-air heat pump is added to complement electric heating the consumption will decrease. However in both cases if the earlier consumption of the primary energy source is compared with the new consumption of electrical energy the consumption is decreased because most of the heating energy of heat pump is coming from ground or from air. Because of decreased overall primary energy consumption also carbon dioxide emissions are decreased depending on how electricity is produced. The greater usage of fossil fuels in electricity production the greater cutting can be achieved using heat pumps.

Heat pumps are also a good example of loads which have become more common because of technical development and reduced manufacturing costs. Nowadays in Finland an air-to-air heat pump costs about 1200-3500 € including installation which is quite feasible price in Finland [5]. Ground source heat pumps cost more because it will need a ground circuit and the device is bigger in the power scale.

Heat pumps and overall new loads are changing the use of electrical energy. Even though these loads may have a favorable effect on overall energy consumption some power quality problems may occur when using these loads. This is mainly caused by the new electrical characteristics of these loads.  The planning principles of distribution networks are becoming old-fashioned and do not always fulfill the requirements of these new loads. From the power quality point-of-view the trickiest part will be the commonness of these loads because it means that power quality problems are also becoming more common.

This paper will study power demand and some power quality problems caused by the use of heat pumps. The study is based on qualitative analysis and practical case study measurements which were carried out in real distribution networks in Finland. In the paper there is first a theoretical examination about power quality problems. After that there is qualitative analysis about power demand and voltage levels. This is followed by a description of case study measurements carried out. Finally there are results and conclusions of those measurements.

# Theoretical backround of power quality

Power quality is defined as “Set of parameters defining the properties of power quality as delivered to the user in normal operating conditions in terms of continuity of supply and characteristics of voltage (symmetry, frequency, magnitude, waveform) in IEC” [7]. In this paper, we are observing power quality in terms of quality of voltage. The limits for voltage quality are defined in standard EN 50160 Voltage characteristics of electricity supplied by public distribution networks. The standards object is to define and describe characteristics of the supply voltage concerning: frequency, magnitude, wave form and symmetry of the line voltages. “These characteristics are subject to variations during normal operation of the system because of changes of load, disturbances generated by certain equipment and the occurrence of faults which are mainly caused by external events”.  Variation of the characteristics is random in time and location. Therefore on small number of occasions the limits can be expected to be exceeded. [8]

The standard EN 50160 defines the characteristics of voltage in low voltage and medium voltage networks [8]. Because we are interested to study power quality problems in customer point of view only the characteristics of voltage in low voltage networks are considered in this paper. Practical case measurements are focusing on a flicker caused by rapid voltage changes because those are a very common cause for power quality complaints as shown in Figure 2. Other problems are discussed qualitatively. Figure 2 presents the distribution of power quality complaints in one distribution utility in Finland during the years 2003-2005. About 44 % of all power quality complaints were caused by flicker. In the Netherland, grid operators’ data base shows that almost 60 % of all power quality complaints concern flicker [11].

Figure 2	Distribution of power quality complaints in one distribution utility in Finland during years 2003-2005 [9].

The other reason to focus only on flicker, when studying power quality, is that devices very commonly cause these disturbances. This mainly happens because a device requires power to operate. In addition voltage, a device will need current from the grid. This current will cause a voltage change over the impedance of a distribution network. This is seen in Equation 1. Depending on the connection of a device it may have different effects to phase voltages.  If the connection is a three-phase connection and connection is symmetrical, all phase voltages will experience the same kind of effect voltage drop or voltage rise. If the connection is a single-phase connection, every phase will experience different kind of voltage change because of the star point displacement for example one could rise and the others drop.

(1)

where	= vector of voltage change

= vector impedance of distribution network

= vector device current

The standard EN 50160 defines permitted levels for a flicker so that 95 % of long term flicker severity in any week should be lower or equal than 1. For voltage levels, standard defines that 95 % of the 10 min mean r.m.s. values of the supply voltage shall be within the range of Un ± 10 % during each one period and all of  10 min mean r.m.s. values shall be within range -15 % < Un < +10%. Exceptions for voltage levels can appear for example in remote areas with long feeder lines or not connected to a large interconnected network. In these cases voltage levels could be outside previous mentioned range but a customer or user should be informed of the conditions. [8]

# theoretical backround of induction motor of heat pump

Ground source and air-to-water heat pumps are mainly equipped with a induction motor. This component is the most significant component in these devices from the power usage and power quality point-of-view. The induction motor is three-phase connected. Generally those heat pumps are directly operated based on network frequency. There are still some ground source and air-to-water heat pumps that are equipped with frequency converter.

The biggest impact of an induction motor on the distribution network appears when the motor is started. The induction motor takes a high starting current. High starting current causes voltage change over the impedance of the distribution network. This phenomenon is seen in Figure 3 and equation 2. Figure 3 a presents an equivalent circuit of a polyphase induction motor and figure 3 b presents an approximate equivalent circuit of a polyphase induction motor. The approximate equivalent circuit is based on assumptions that the reactive component of impedances z1 and zm is much greater than the resistive component and the voltage E2 is only little smaller and nearly in the same phase with voltage V. These assumptions are valid in conventional induction motors in the normal running range. Equation 2 can be defined from figure 3 b. From Equation 2 can be seen that when the slip of the induction motor is small the motor takes a high current from a network. The slip is 1 at the moment of starting the induction motor and will decrease close to 0 after a starting. [10]

Figure 3	a) Equivalent circuit of three-phase induction motor b) Approximate equivalent circuit of a three-phase induction motor [10]

(2)

resistance of stator

leakage reactance of stator

magnetizing reactance

resistance of rotor

leakage reactance of rotor

slip of motor

The starting current causes remarkable power quality problems when using induction motors because current reaches highest value at the beginning of start up and it won’t fluctuate much during normal operation. From flicker point-of-view, the critical factor is how often the motor is needed to start up. If the start up frequency is very high more voltage changes will appear. For the heat pumps length of the running cycle depends on the need of the heating energy, the dimensioning and parameter settings of a heat pump. If the heating power demand is close to the nominal heating power of the heat pump, the pump may run long times continuously. If the heating power need is clearly lower than the nominal heating power of the heat pump, stopping and reclosing of the pump will appear. The time between the stopping and reclosing the pump depends on the restrictions of the process and, for example, for one ground source heat pump the shortest time between stopping and restarting the process is 10 minutes according to a heat pump supplier.

# Preliminary analysis of the impacts of the penetration of heat pumps on the total power demand and voltage level in distribution networks

This part of the examination is done in qualitatively because it is not possible to deduce the impacts of penetration of heat pumps in numbers on the total power demand everywhere in the distribution network. Guidelines for impacts can still be analyzed.

The heating power produced by a heat pump depends on the type of heat pump and an outside temperature. Normally if a ground circuit of a ground source heat pump is dimensioned adequately a ground source heat pump will produce nominal heating power during the maximum heating demand in other words during the coldest time of the year. There are two different sizing methods for ground source heat pumps. One is fully dimensioned and the other is partially dimensioned heat pump. When, the ground source heat pump is fully dimensioned, the maximum heating demand of a building is lower than the maximum heating supply of a heat pump. If special superheating technique is used also use water can be warmed up without any other energy sources. When, the ground source heat pump is partially dimensioned, the maximum heating demand of a building is higher than the maximum heating supply of a heat pump. In this case, the heating power difference needs to be generated with other energy sources. The most common way to do it is to use electric heating. Also burning oil or wood can be used for complement the heating power difference.

For air-to-air and air-to-water heat pumps heating power production and coefficient of performance (cop factor) are highly dependent of the outside temperature. Both of those will drop when the temperature falls too low. Basically when the temperature is lower than -15 C° - -20 C° the air-to-air and air-to-water heat pumps needs to be stopped. This means that there is a need for other fully dimensioned heating system in addition to these heat pumps. A very common way to do it is to use electrical heating but also, as it was for ground source heat pumps, e.g. oil or wood heating can be used.

The effect on electrical power demand in distribution networks depends on the number of heat pumps in the distribution network, what kind of heating system heat pumps have replaced or complemented, heat pumps type, how heat pumps are dimensioned, how heating systems are dimensioned, how the maximum heating power demand is produced and how heat pumps are operated. The maximum electrical power demand will occur during winter time when the outside temperature is the lowest at least in Finland. In general if heat pumps are replacing or complementing other than electrical heating systems the maximum electrical power demand increase with the exception of air-to-air and air-to-water heat pump systems that are using other than electrical energy to meet maximum heating power demand.

Electrical power demand can also decrease. In general this happens when electrical heating systems are replaced ground source heat pumps. If a ground source heat pump is fully dimensioned, it will decrease electrical power demand for heating. If a ground source heat pump is partially dimensioned, it can decrease or increase maximum electrical heating power demand. This depends on how the difference between maximum heating demand of a building and maximum heating supply of a heat pump is generated. If this difference is generated with electric heating, it might increase maximum heating power demand. This depends on how powerful additional electrical heating is and how it is operated.  If the additional electric heating is large enough and it is operated during maximum heating power demand so that all electrical heating power is connected to network it could also increase maximum electrical power used for heating.

In cases where electrical heating systems are complemented with air-to-air or air-to-water heat pumps the maximum electrical demand for heating doesn’t change because such heat pumps cannot generate heat when the temperature has decreased too low.

The most problematic places at a increased power demand point of view might be distribution networks where numerous other than electrical heating systems are replaced with heat pumps that are using electrical heating to meet the maximum heating demand. The worst case scenario is a distribution network where, for example, numerous oil heating systems are replaced by air-to-water heat pumps and the maximum heating demand is generated with electrical heating. Now all of those houses are acting as electrical heating systems and maximum power demand might be increased remarkably. In these cases power demand growth can act like step function because neighbors can encourage one another to replace oil heating systems in very short time scale if it is compared with a distribution networks lifetime. This power demand growth can lead to the exceeding of components current carrying capacity but also it can lead to dramatic voltage level drops at the end of low voltage lines.  It is possible that in those places distribution networks needs to be reinforced before a designed schedule. Also networks that are feeding summer cottages might face this problem.

In other networks where both electrical heating and other heating sources are replaced and complemented by heat pumps the increase of maximum electrical power demand for heating can be restrained by the negative effect of ground source heat pumps. This depends on how much replacements have happened and what kind of heat pumps have come to network. Even though in these places exceeding of current carrying capacity might not be a problem during distribution networks lifetime but voltage level problems may still occur at the end of low voltage line.

One way to get some idea how much power demand could increase in distribution networks because of heat pumps is to consider the estimation of how much electrical power demand is increasing at system level. This estimation is shown in Figure 4_1. Figure 4_1 shows estimated maximum electrical power growth caused by the penetration of heat pumps at system level. This Figure doesn’t include the new building or the improvements of the energy efficiency of the building stock. Used maximum power is segregated for different heating types that they are using in 2010.  From Figure 4_1, we can see that maximum electrical power demand is estimated to increase almost 11 % in 20 years at system level. This can be taken some sort of guideline for increasing of power demand but in distribution network this can be higher or lower depending on previously mentioned factors.

Figure 4_1. Estimated impact of the penetration of heat pumps on the total power demand in system level

# Description of Practical case measurement study

In our study, two practical case measurements were made in Finland one in Tampere and the other in Kymenlaakso region. In both cases the scope and the environment were bit different. Dranetz PX-5 power quality analyzer and Dranetz 4400 power quality analyzer and a oscilloscope Lecroy (LT354) were used as measuring devices in our study. In this chapter both practical case measurements will be described in depth.

Tampere urban area network

In Tampere the scope of the study was to explore power quality problems caused by ground source heat pumps in an urban area network. Feeders in this low voltage network were mainly underground cables with cross-sections from 300 mm2 to 120 mm2 and the rated power of 20/0.4 kV transformer was 315 kVA.  In this low voltage network computational single phase short circuit currents varied from 9,7 kA to 445 A and three phase short circuit currents varied from 10.8 kA to 1110 A so the network was quite strong. At the one end of this low voltage network two terrace houses changed their shared oil heating system into a separate ground source heat pump systems. The installation was made so that two ground source heat pumps, nominal heating powers 25 kW and 36 kW and maximum electrical powers 9,9 kW and 13,2 kW, were installed to both terrace houses. Starting of all heat pumps was direct on line starting so every time heat pumps were started a high starting current appeared. This place was selected to this study because some customers in both terrace houses complained about flicker. Overall picture of low voltage network, customer supply terminal short circuit currents and measuring points are illustrated in figure 4. Measured quantities were voltage and current waveforms and quantities defined in standard EN 50160.

Figure 4. Overall picture of the low voltage network in Tampere with measuring point locations

Kymenlaakso region rural area network

In Kymenlaakso region the scope of the study was to exploit power quality problems caused by different ground source heat pumps in a rural area networks. Measurements were performed in many different low voltage networks where feeders were mainly aerial bundled cables called AMKA. Specifications of different low voltage networks and type of heat pumps are showed in Table 1. In each place measurements were only performed in a customer supply terminal. In some places measurements covered overnight measurement and in some places only few starting ups of heat pump were recorded. Measured quantities were voltage and current waveform and quantities of standard EN 50160.

Table 1	Specifications of different low voltage networks in Kymenlaakso region.

|  |  |  | Network information |  |
| --- | --- | --- | --- | --- |
|  | Heat pump type | Softstarter | Nominal power of distribution transformer [kVA] | Calculated single pahse short circuit current Ik1 at customer supply terminal [A] | Calculated three pahse short circuit current Ik3 at customer supply terminal [A] | Running cycle and flicker measurement |
| Heat pump 1 | GS | n | 200 | 257 | 628 |  |
| Heat pump 2 | GS | y | 200 | 257 | 628 | x |
| Heat pump 3 | GS | y | 200 | 286 | 628 | x |
| Heat pump 4 | GS | y | 100 | 283 | 606 |  |
| Heat pump 5 | GS | y | 100 | 446 | 1031 | x |
| Heat pump 6 | GS | y | 100 | 364 | 790 |  |
| Heat pump 7 | GS | y | 100 | 273 | 620 | x |
| Heat pump 8 | GS | n | 50 | 275 | 516 | x |
| Heat pump 9 | GS | n | 100 | 343 | 686 |  |
| Heat pump 10 | GS | y | 200 | 350 | 851 |  |
| Heat pump 11 | GS | y | 200 | 265 | 680 | x |
| Heat pump 12 | GS+EA | n | 50 | 221 | 446 | x |
| Heat pump 13 | GS+EA | n | 100 | 207 | 462 |  |

# Practical case study results

In this chapter it is presented the results of practical case studies. This chapter is headlined similarly than previous chapter so that it is easy to follow results.

Tampere urban area network

In Tampere four heat pumps were operated in the same low voltage network. The measurement period was one week. During this period, the mean temperature of a day was 3...9 °C and at night the temperature fell under 0 °C. This meant that heating power need was not near heating capacity of pumps so start ups and stops of pumps should appear. Installations of pumps were made so that a bigger pump heated only a water circulation of radiators. A smaller pump heated mainly use water but could support a bigger pump to heat a water circulation of radiators. Because of a direct on line start up of pumps high starting currents were detected. Starting currents of bigger pumps were 220...230 Arms and duration were approximately 4 cycle. Starting currents of smaller pumps were 185...195 Arms and duration were approximately 3 cycle.

Running cycle of pumps varied between terrace houses. The bigger pump of customer 1 ran typically from 1 h to 3 h 20 min.  Time between two start ups varied from 1 h 40 min to 4 h 10 min and the average time between two start ups was 2 h 20 min. The total number of start ups was 73. The bigger pump of customer 2 ran typically from 50 min to 11 h. Start up times of bigger pump of customer 2 varied from 2 h 20 min to 12 h 10 min and the average time between two start ups was 3 h 50 min. The total number of start ups was 43. In both cases, the biggest running times appeared at night time and shorter ones at day time. This is due to a bigger heating need at night time. The differences between running times of bigger pumps could derive from the different size of houses and different heating system specifications.

Because of current measurement were placed in a shared feeder of different size heat pumps, running times of smaller pump was difficult to define. Start up times could still be defined. For a smaller pump of customer 1 time between two start ups varied from 19 min to 2h 10 min and the average time between two start ups was 39 min. The total number of start ups in one week was 255. For a smaller pump of customer 2, time between two star ups varied from 24 min to 1 h 40 min and the average time between two start ups was 30 min. The total number of start ups in one week was 371.

The total number of different heat pump start ups in a specific hour of customer 1 during one week is shown in Figure 7. Figure 7 is presenting the number of start ups so, that if a smaller pump of customer 1 has started up once every day between 8.00 am and 9.00 am the number for smaller pump of hour 8.00 will be 7. As shown in Figure 7, start ups of the smaller heat pump most commonly occurred at evening and day time. At night time, the number of star ups of the smaller pump decreased significantly. This happened because there was used more use water at day and evening time than at night time. For the bigger pump there was no specific time for start ups, only there was less start ups at morning. This appeared because the heat pump ran longer at morning. This was because of the bigger heating power need due to decreased the outside temperature. Because of this kind of distribution in start up times, there was a lower long term severity flicker index at night than day time. The key issue of a high short term flicker index was bigger pump start up time and common star ups in the same 10 minute for both heat pumps of customer 1. Also if there was common start in the same 10 minute for heat pumps of customer 2, it raised a short term flicker severity index above 1, which is irritation threshold.

Figure 7. The total number of different heat pump start ups in specific hour of customer 1 during one week

The total number of heat pump start ups in a specific hour of customer 2 during one week is shown in Figure 8. As shown in Figure 8 there were more start ups of the smaller pump for customer 2 than customer 1. The number of start ups stayed quite high all day around. There were just little less start ups at night time than day time. For the bigger heat pump there were just a few start ups during the whole week. This was because of long running times of the bigger heat pump. The long term flicker severity index got higher values at evening than night time because of this kind of distribution at start up times of different heat pumps. For high short term flicker severity index the key issues were the same for customer 2 than customer 1. The start up of the bigger heat pump of customer 2 meant a higher short term flicker severity index of customer 2 and if there was start up of the both bigger and smaller heat pumps of customer 2 in the same 10 minute a short term flicker severity index got even higher. Also if there was start up of both heat pumps of customer 1 short term flicker severity index raised above 1. In Table 3 it is gathered up short term flicker severity indices at the different customer end when different heat pumps started up. Short term flicker severity indices are average 10 minute values of events mentioned in the Table 3. Table 3 shows previous mentioned cross disturbance from the heat pump of one customer to the short term flicker severity index of other customer. Table 3 also shows the bigger effect of the bigger heat pump start up to the short term flicker severity index.

Figure 8. The total number of different heat pump start ups in specific hour of customer 2 during one week

Table 3. Average values of short term flicker severity index at different customer end when different heat pump is or pumps are started up

| Start up of |
| --- |
|  | Smaller heat pump of customer 1 | Bigger heat pump of customer 1 | Both heat pumps of customer 1 | Smaller heat pump of customer 2 | Bigger heat pump of customer 2 | Both heat pumps of customer 2 |
| Customer 1 Pst | 0.88 | 1.04 | 1.52 | 0.66 | 0.81 | 1.20 |
| Customer 2 Pst | 0.69 | 0.80 | 1.21 | 0.80 | 0.98 | 1.41 |

Even though there were sometimes relatively high short term flicker indexes the long term flicker index never during one week did not exceeded level 1. The highest long term flicker severity index was 0.99 at customer 1 end.  The standard EN 50160 defines threshold levels to the flicker so that “under normal operating conditions, in any period of one week the long term flicker severity caused by voltage fluctuation should be Plt ≤ 1 for 95 % of the time”. This means also that threshold defined in standard was not exceeded.

Despite the fact that flicker did not exceed the threshold level of standard EN 50160, flicker from heat pumps start ups was clearly visible. The start ups of heat pumps were easily seen from lighting. Some customers can be irritated from rapid voltage changes of this kind. Now at the distribution utility point of view it is easy to say that no problems occurred and the case is closed. At customer point of view there might be flicker problems so the result there cannot be a flicker is not a good answer from a customer service point of view. In this case, the result was that the manufacturer of all these heat pumps will install softstarters to heat pumps.

Kymenlaakso region rural area network

In Kymenlaakso region 13 different ground source heat pumps were measured in rural area networks during winter time. Most of these pumps were measured in February. The outside temperature varied from -17 °C to -3 °C during measurement period. This meant that the heating power need was quite high. Depending on design of different heat pumps the heat power need could be near than heat power production of heat pump so start ups of pumps should appear but not as much as measurement in Tampere.

For some heat pumps there were made measurements that covered only few start ups of a heat pump and for others there were made overnight measurements. From pumps 4,5 and 8 the starting current waveforms per phase are presented in Appendix 1-3. Appendixes 1 and 2 show the starting current waveform when there is installed softstarter in heat pump. The starting current is not fundamental sine wave. Appendix 3 shows starting current of heat pump which start is direct on line start. In this case the starting current is fundamental sine wave. The starting current lasts longer, approximately 10 cycles, when there was softstarter. With direct on line starting the starting current lasts approximately 3 cycles.

The overall data from heat pump measurements is gathered in Table 4. Table 4 shows for every heat pump: the heat pump type, nominal heating power and electric power according to manufacturers brochure, if heat pump is equipped with softstarter or not, starting current according to manufacturers brochure and according measurements, ratio between highest starting current and three phase short circuit current in percent value, and if flicker problem was detected. Heat pump 1 and 2 are the same pump measured with and without softstarter. Also heat pump 3 was connected in the same low voltage network than heat pump 1 (and 2).

Table 4. Overall results of measurement of heat pumps in rural area networks in Kymenlaakso region

|  |  | Power information |  | Starting current |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Heat pump type | Heat power 0/+35 °C [kW] | Electric power 0/+35 °C [kW] | Softstarter | Starting current RMS according to manufacturer [A] | Measured starting current RMS I1rms [A] 3) | Highest measured starting current RMS value I1maxrms [A] | Highest I1rms/Ik3 [%] | Additional heating resistor [kW] | Flicker problem was detected |
| Heat pump 1 | GS | 16,7 | 3,57 | n |  | 55 | 57 | 9,08 |  | X |
| Heat pump 2 | GS | 16,7 | 3,57 | y |  | 42 | 48 | 7,64 |  | X |
| Heat pump 3 | GS | 11,4 | 2,42 | y |  | 30 | 38 | 6,05 |  | X |
| Heat pump 4 | GS | 14,2 | 3,03 | y | 45 | 47 | 52 | 8,58 |  | X |
| Heat pump 5 | GS | 11,4 | 2,42 | y | 37 | 36 | 39 | 3,78 |  |  |
| Heat pump 6 | GS | - | - | y |  | 33 | 34 | 4,30 |  |  |
| Heat pump 7 | GS | 8,8 | 1,9 | y | 24 | 16 | 22 | 3,55 | 6 (9) |  |
| Heat pump 8 | GS | 11 | 2,7 | n | 50 | 35 | 38 | 7,36 | 6 |  |
| Heat pump 9 | GS | 7,5 | 1,8 | n | 39 | 30 | 30 | 4,37 | 6 |  |
| Heat pump 10 | GS | 10,8 | 2,4 | y | 20 | 15 | 16 | 1,88 | 3/6/9 |  |
| Heat pump 11 | GS | - | - | y |  | 30 | 30 | 4,41 |  |  |
| Heat pump 12 | GS+EA | 4,0 1) | 1,4 2) | n | - | 27 | 28 | 6,28 | 9 | X |
| Heat pump 13 | GS+EA | 4,0 1) | 1,4 2) | n | - | 27 | 27 | 5,84 | 9 |  |
| 1) Heat power 0/+45 °C | 2) Nominal power of compressor | 3) Mean value of three phase starting currents |

It is seen from these measurements, that heat pumps are not very critical loads in rural area networks at a flicker point of view. In three different low voltage networks a short term flicker index was over 1. In two of those places, a long term flicker index was quite often also above threshold level 1. One of these places there were at least two ground source heat pumps in the same low voltage network, namely heat pump 1 (and 2) and heat pump 3. In this case, both heat pumps increased each other flicker level. In the other long term flicker problem case, namely heat pump 12, it was not possible to deduce that the heat pump was the reason for a flicker problem based on the measurements. The third problem, namely heat pump 4, concerned only a short term flicker index. In this case long term flicker severity index was clearly below 1.

From the measurements could be seen that there are quite big differences in starting currents between different manufacturers when nominal heating and electrical power are almost the same. This occurs because softstarters are constructed very differently in different heat pumps. One key result from the measurements was that when starting current was 8-10 % of the three phase short circuit current the probability for flicker problems increase in a significant level. In these cases, attention should pay to a starting current to decrease possibility for flicker problems. This is also a very useful result for distribution utilities to give guidance to customers who are asking permission to connect heat pumps in the distribution network. Also there should be notice that the percent number will decrease when more than one ground source heat pump is connected to the same low voltage network.

# Conclusions

In this paper there were examinations about power demand and power quality problems caused by ground source heat pumps. The examination is based on practical case measurements made in real distribution network in Finland.

Electrical power demand for heating can increase or decrease at distribution network level by the penetration of heat pumps. The most probable scenario is that maximum electrical power demand will increase but it will not exceed network limits. In distribution networks where numerous other than electrical heating systems are replaced with heat pumps, especially oil heating with air-to-water heat pumps and maximum heating demand is generated by an electric heating, network current capacity limits may be exceeded during a networks designed lifetime. In addition voltage levels at the end of low voltage line may drop remarkably in some distribution networks due to heat pumps maximum power demand.

Power quality problems caused by heat pumps were studied in two different kinds of networks in urban area and rural area networks. In urban area network there was four big heat pumps installed into two terrace houses. Here start ups of heat pumps caused short term flicker index increasing over irritation threshold 1. Also start ups of heat pumps in one terrace house increased other terrace houses short term flicker index over 1 so there was cross disturbing from one terrace house to other. Even though the short term flicker index was sometimes over 1 the long term flicker index was always under 1 so in standard point of view there was no flicker problem. Despite this every star up of heat pumps could easily saw from lighting so someone could feel this to be irritating. In this case the result was that manufacturer of all these pumps will install softstarters to all heat pumps.

In this paper there were studied also power quality problems caused by heat pump in rural area networks. This examination based on measurements which were performed in many different rural area low voltage networks in Kymenlaakso region. In rural area networks power quality problems caused by heat pumps were quite minimal. In three places the short term flicker index was over 1. It seems that nowadays when there is only one or two heat pump connected to same low voltage network power quality problems, especially flicker problems, stays very low. But number of heat pumps is increasing so in the future there might be low voltage networks in which there are connected several heat pumps. This can increase power quality problems because start ups of heat pumps can disturb voltage quality in nearby customer supply terminals and number of start ups will also increase.

[1] 	 European lamps become more energy efficient. [WWW]. [Cited   7/4/2010]. Available at: http://ec.europa.eu/energy/efficiency/ecodesign/lumen/doc/incandescent-bulbs-en.pdf

[2] 	Sulpu. Finnish heat pump association. [WWW]. [Cited   7/4/2010].   Available   at: http://www.sulpu.fi/images/stories/10v_seminaari/sulpu_jussi_hirvonen_esitys_10v.pdf

[3]	 European Heat Pump Statistics Outlook 2008. European heat pump association. [WWW]. [Cited   7/4/2010].   Available   at: http://www.ehpa.org/fileadmin/red/Heat_Pump_Statistics/European_Heat_Pump_Statistics_2007.pdf

[4] 	Finnish government notice. [WWW]. [Cited 31.5.2010]. Available   at: http://www.vn.fi/ajankohtaista/tiedotteet/tiedote/fi.jsp?oid=236864

[5] 	The great price comparison of air heat pumps. [WWW]. [Cited 31.5.2010]. Available   at: http://www.co2-raportti.fi/index.php?page=ilmastovinkit&news_id=735

[6] 	Official Journal of the European Union- Commission Regulation (EC) No 244/2009

[7]	Math H. J. Bollen. Understanding Power Quality Problems. Voltage Sags and Interruptions. Gothenburg 2000. IEEE Press. p. 543

[8]	EN 50160. European Standard. Voltage characteristics of electricity supplied by public distribution networks. 2004.

[9]	Suurinkeroinen, Seppo. Presentation. Luosto Power Quality Seminar 2007.

[10] 	Matsch, L. Morgan , D. 1987. Electromagnetic and electromechanical machines. Third

Edition. New York. John Wiley & Sons. 566 p.

[11]	Rong Cai. Flicker Interaction Studies and Flickermeter Improvement. the Eindhoven University of Technology 2009. Doctoral dissertation work. p. 176.

# appendix 1: Starting current waveform of heat pump 1. Ch1 is phase L1, Ch2 is phase L2 and Ch3 is phase L3

# appendix 2: Starting current waveform of heat pump 2. Ch1 is phase L1, Ch2 is phase L2 and Ch3 is phase L3. One volt correspond one ampere

# appendix 3: Starting current waveform of heat pump 3. Ch1 is phase L1, Ch2 is phase L2 and Ch3 is phase L3. One volt correspond one ampere.